## 工作表1
1kwh | 3.6MJ
kwh/m2
Month | Num of Day | Daily Mean Horizontal Solar Irradiation (kWh/m2/day) | Cumulative | cityu weather
January | 31 | 2.82 | 87.42 | 78.701
February | 28 | 2.75 | 77 | 75.371
March | 31 | 2.82 | 87.42 | 90.113
April | 30 | 3.29 | 98.7 | 101.104
May | 31 | 3.91 | 121.21 | 113.78
June | 30 | 3.97 | 119.1 | 115.678
July | 31 | 4.6 | 142.6 | 152.7
August | 31 | 4.23 | 131.13 | 134.262
September | 30 | 4.01 | 120.3 | 119.987
October | 31 | 3.95 | 122.45 | 125.499
November | 30 | 3.44 | 103.2 | 103.82
December | 31 | 2.98 | 92.38 | 94.766 | 863.01
| 365 |  | 1302.91 | 1305.781
|  | conversion rate | 9.3%
|  | PV solar energy | 121.1706 | kwh/m2/yr
Simple Rectangular Building
Time Period | April 1 to Oct 31
| Diffuse Irrad | Direct Irrad | Global
| wh/m2 | wh/m2 | wh/m2 | kwh/m2
Top Surface | 489902.4 | 296118.5 | 786020.9 | 786.0209
N | 196354 | 79452.38 | 275806.38 | 275.8064
S | 221517.1 | 84099.45 | 305616.55 | 305.6165
E | 206698.1 | 54001.24 | 260699.34 | 260.6993
W | 208542.9 | 348853.7 | 557396.6 | 557.3966
| Area Weighting | Vertical Façade Average |  |  |  | Baseline | 80% of Baseline
N | 1 | 349.8797 | kwh/m2 |  | BEAM EU1a | 395 | 316
S | 1
E | 1
W | 1

## Sheet1
|  | area | irrad - w/m2 | per area - w/m2 | per area - kw/m2 | annual averaged daliy - kwh/m2
| Horizontal Plane | 10.9685 | 9678934.4773 | 882431.9419 | 882.4319 | 2.4176
Vertical - N | P0_0 | 4 | 1475482.5457 | 368870.6364 | 368.8706 | 1.0106
| P10_0 | 4 | 1441888.7102 | 360472.1621 | 360.4722 | 0.98759
| P20_0 | 4 | 1429168.7882 | 357292.1717 | 357.2922 | 0.97888
| P30_0 | 4 | 1435348.3446 | 358837.0725 | 358.8371 | 0.98312
| P40_0 | 4 | 1445060.4998 | 361265.1125 | 361.2651 | 0.98977
| P50_0 | 4 | 1457316.8386 | 364329.1971 | 364.3292 | 0.99816
| P60_0 | 4 | 1473178.1433 | 368294.5218 | 368.2945 | 1.009
| P70_0 | 4 | 1488829.5208 | 372207.3538 | 372.2074 | 1.0197
| P80_0 | 4 | 1506847.8941 | 376711.9574 | 376.712 | 1.0321
Vertical - E | P90_0 | 4 | 1527214.3436 | 381803.5859 | 381.8036 | 1.046
| P100_0 | 4 | 1547431.6197 | 386857.8883 | 386.8579 | 1.0599
| P110_0 | 4 | 1568633.3746 | 392158.3159 | 392.1583 | 1.0744
| P120_0 | 4 | 1591338.983 | 397834.7306 | 397.8347 | 1.09
| P130_0 | 4 | 1617137.015 | 404284.2398 | 404.2842 | 1.1076
| P140_0 | 4 | 1645240.729 | 411310.168 | 411.3102 | 1.1269
| P150_0 | 4 | 1677807.1563 | 419451.7731 | 419.4518 | 1.1492
| P160_0 | 4 | 1720718.7693 | 430179.6618 | 430.1797 | 1.1786
| P170_0 | 4 | 1770402.9272 | 442600.7128 | 442.6007 | 1.2126
Vertical - S | P180_0 | 4 | 1825462.4793 | 456365.6198 | 456.3656 | 1.2503
| P190_0 | 4 | 2277700.3834 | 569425.0714 | 569.4251 | 1.5601
| P200_0 | 4 | 2449173.116 | 612293.2356 | 612.2932 | 1.6775
| P210_0 | 4 | 2640279.249 | 660069.7871 | 660.0698 | 1.8084
| P220_0 | 4 | 2797304.7463 | 699326.1624 | 699.3262 | 1.916
| P230_0 | 4 | 2922305.5658 | 730576.3662 | 730.5764 | 2.0016
| P240_0 | 4 | 3004553.5263 | 751138.3529 | 751.1384 | 2.0579
| P250_0 | 4 | 3040751.324 | 760187.7771 | 760.1878 | 2.0827
| P260_0 | 4 | 3031054.8217 | 757763.6729 | 757.7637 | 2.0761
Vertical - W | P270_0 | 4 | 2985399.1489 | 746349.7872 | 746.3498 | 2.0448
| P280_0 | 4 | 2888716.0138 | 722178.9725 | 722.179 | 1.9786
| P290_0 | 4 | 2758183.0012 | 689545.7014 | 689.5457 | 1.8892
| P300_0 | 4 | 2589217.9403 | 647304.4604 | 647.3045 | 1.7734
| P310_0 | 4 | 2396262.5 | 599065.6043 | 599.0656 | 1.6413
| P320_0 | 4 | 2187833.6587 | 546958.3958 | 546.9584 | 1.4985
| P330_0 | 4 | 1984368.1384 | 496092.0157 | 496.092 | 1.3592
| P340_0 | 4 | 1800425.8458 | 450106.4295 | 450.1064 | 1.2332
| P350_0 | 4 | 1648271.1466 | 412067.769 | 412.0678 | 1.129

## Sheet2
Knowledge:
Peak Hours -峰值日照小时数 | All Day Radiation (Wh/m2) | Conversion (W/m2)
6 | 6000 | 1000
什麽是KWP？
PV System Capacity (kw) | Sys Efficiency |  | Watt-peak或Wp是太陽能板的直流額定額定值
2000 | 0.8 |  | 在標準測試條件下（通常稱為STC）的額定峰值直流輸出功率。 STC（Standard Testing Condition）指的是1000 W/m2的輻照度，光伏電池篇溫度為25℃，空氣質量為1.5。太陽輻照度為1000 W/m2，大約在中午時分發生，因此大部分時間，輻照度將低於1000 W/m2，也就是太陽能板的淨輸出功率， 除了在中午時分之外， 大部分時間都將在STC額定功率值之下。
在熱天，太陽能板溫度也可能上升到65攝氏度，因此太陽能電池板的輸出功率也會比STC的額定值低。
PV electricity generation (kwh) |  |  | 因此太陽能板的STC額定功率值， 或者說在太陽能板標記銘牌的額定功率值是理想狀態的功率值。 而在實際操作中，實際的功率會比額定功率低。大多數已建立的系統集成商在計算光伏系統的估計能量產量時，都應該考慮這些減量。
9600 |  |  | 1 kWp = 1000 Wp。如果一個太陽能電池板的額定功率是350瓦，那麼一個100片太陽能板的系統= 100×350 = 35000瓦= 35千瓦。
PV product:
STC - standard test condition | rated power - 额定功率 (W) | 350
1000 W/m2 irradiation | Dim (m2) | 1.7272
Cell Termperature 25 degC | Cells | 6*10
AM-空氣質量 1.5 | cell area (m2) | 0.026147
| 0 - 25 yrs | 88.4% or above of initial power
HK annual radiation (kwh/m2) | 1300 | 1427.15
Annual peak hour | 1300
Electricity Per Unit PV (kw) | 364
Electricity Per area PV (kw/m2) | 210.7457
Solar Radiation to Electricity Ratio | 16.21%
由於香港位於北緯22度，所以面板必須面向南， 傾斜17-18度為最佳
| Equipment Cost | Efficiency - Solar Radiation to Electricity Ratio
Mono-crystalline | 24 - 40 hkd per watt | 20% - 25%
Poly-crystaline | 24 - 40 hkd per watt | 10% - 24%
Amorphous silicon (Thin-film) | 16 - 24 hkd per watt | 6% - 9%